## Sheet1
Attachment A: Cost Sheet
AM2026 OR : Manufactured Climate-controlled Shelter for Ambient Air Monitoring Equipment
SHELTER CONSTRUCTION AND EXTERIOR FEATURES
Line # | Item | Quantity | Unit Cost | Total Cost
a | Shelter shall be solidly constructed, self-supporting, and water-tight Dimensions: 8 ft wide x 8 ft deep x 8 ft high Exterior cladding: aluminum with ivory or cream finish Interior cladding: fiberglass with white finish | 1
b | R-25 insulation in walls, ceiling, and floor; average U-factor for wall and roof less than 0.200 | 1
c | Aluminum C-channel skid runners on base of shelter | 2
d | Lifting/anchor ring/point at each corner of base of shelter | 4
e | Roof: topmost layer white membrane compliant with 2018 International Energy Conservation Code solar reflectance and thermal emittance requirements for Climate Zone1 | 1
f | Insulated metal access door, 36 in wide, with wind restraint and commercial lever handle with lock | 1
g | Aluminum modular roof railing system with safety gate compliant with OSHA regulations | 1
h | Vertical exterior ladder for roof access affixed to side of shelter | 1
i | Slip-resistant aluminum roof grating | 1
j | Roof hole and feed-through plate sized to fit MetOne BAM 1020 intake, with intake support bracket attached to roof guard rail | 1
k | Ambient air intake manifold installed through roof with Teflon-lined tubing to supply three gas analyzers | 1
SHELTER HVAC, ELECTRICAL SYSTEMS, AND OTHER INTERIOR FEATURES
Line # | Item | Quantity | Unit Cost | Total Cost
a | Combined 1-ton (12,000 BTU) Cooling / 3,000-watt heating, 208/240V, 20-amp hardwired, with autoswitching thermostat and automatic condensate disposal system | 1
b | 100A, 1 phase, 120V electrical system with load center | 1
c | 100A, 1 phase, 240V external disconnect with NEMA 3R enclosure | 1
d | 20A, 120V duplex interior receptacles | 3
e | Interior ceiling lights (LED) with wall switch | 2
f | Seamless vinyl flooring | 1
g | 8-ft workbench, 24 to 27” deep | 1
h | Gas bottle (tank) supports with straps | 4
i | Wall vent with screened hood | 1
SHELTER ENGINEERING AND FREIGHT COSTS
Line # | Item | Quantity | Unit Cost | Total Cost
a | Professional engineer costs for energy analysis | 1
b | Freight cost to South Omaha | 1