## Project Templates & Metrics
PROJECT TEMPLATES AND METRICS
ENERGY EFFICIENCY WORKFORCE DEVELOPMENT AND TRAINING
Number of staff trained | Number of training sessions
Number of apprentices trained | Number of staff hired
HEATING, COOLING, AND VENTILATION
Air Source Heat Pump | Gas Furnace
Quantity, make, model numbers, size | Natural gas or propane
Energy efficiency ratings - including SEER2, EER2, HSPF2, and COP | Quantity, size, and energy efficiency rating
*Requires backup heat source | Hot Water Boiler System
Geothermal Heat Pump | Natural gas or propane
Quantity, make, model numbers, size | Quantity, size, and energy efficiency rating
Energy efficiency ratings - including SEER2, EER2, HSPF2, and COP | Radiant Heating System
*Requires backup heat source | Natural gas or propane
Central Air Conditioner | Quantity, size, and energy efficiency rating
Quantity, make, model numbers, size | Electric Resistance Heating System
Energy efficiency ratings - SEER2 | Make, model number, kW
Packaged Terminal Heat Pump or Air Conditioner | Other
Quantity, make, model numbers, size, and EER | Variable Frequency Drive - quantity, make, and model number
Programmable Thermostat or Digital Controls | Energy Recovery Ventilator - quantity, make, model number, and efficiency rating
Quantity, make, and model number | *See HVAC Requirements Sheet for Equipment Specific Requirements
LIGHTING
Street Lighting* | Building Lighting*
Number of energy efficient streetlights installed | Number of buildings retrofitted
Number of energy efficient street signs installed | Square footage of buildings retrofitted
Traffic Lighting* | Estimated project savings ($) annually
Number of energy efficient traffic signals installed | Estimated project savings (kWh of electricity) annually
Number of street lane-miles for which synchronized traffic signals were installed | *COMPLETE LIGHTING WORKSHEET FOR ALL LIGHTING PROJECTS
BUILDING ENVELOPE IMPROVEMENTS
Insulation and Weatherization | Replacement of Windows and Doors
Type, R-Value, square feet of insulation replaced | Quantity and details of windows and doors to be replaced
Type, R-Value, square feet of insulation added | New window or door details, including number, size, U-Factor
Type, square feet, placement of weatherstripping added | *All windows and doors must be certified by the National Fenestration Rating Council (NFRC)

## HVAC Requirements
Space Cooling |  |  | Space Heating
Equipment Type | Capacity kBtu/hr | Energy Efficiency Requirements | Equipment Type | Capacity | Energy Efficiency Requirements
Central Air Conditioner | < 65 | 16 SEER2 | Forced Air Gas Furnace | All sizes | 95 AFUE
| ≥ 65 and < 135 | 11.2 EER
| ≥ 135 and < 240 | 11.0 EER | Hot Water Boiler and Combined Water and Space Heating | All sizes | 95 AFUE
| ≥ 240 | 10.0 EER
| All Water Cooled and Evaporatively Cooled | 14.0 EER | Radiant Heating System (High Bay Only - 12ft.) | All sizes | 85 Thermal Efficiency
Air Source Heat Pump | < 65 | 10 EER2, 15.2 SEER2, 8.1 HSPF2, and 1.75 COP at 5°F | Electric Resistance | All sizes | Emergency Replacement Systems Only
| ≥ 65 and < 135 | 11.2 EER and 3.4 COP
| ≥ 135 and < 240 | 11.0 EER and 3.3 COP | Heat or Energy Recovery Ventilators |  | ≥ 25% Recovery Efficiency or ≥ 76 @ 75% flow AHRI Total Efficiency
| ≥ 240 | 10.0 EER and 3.3 COP
| All Water Cooled and Evaporatively Cooled | 14.0 EER and 3.3 COP
Additional Requirements
Ground Water or Ground Coupled Heat Pump | All Sizes
| Water Loop | 14.0 EER and 4.6 COP | 1. Condensing type gas units must have combustion intake air ducted from outdoors.
| Ground Water | 16.2 EER and 3.6 COP | 2. Heat pumps must be installed with a ramp-up type thermostat especially designed to bring on backup heat in stages , and only when the heat pump can no longer keep up with demand, and must be able to differentiate between a demand and a 'return' from setback call for heat.
| Ground Loop | 14.1 EER and 3.3 COP
| Direct Exchange | 15.0 EER and 3.5 COP
3. Roof top units must be either cooling only, or meet both heating and cooling requirements.
Packaged Terminal Heat Pump or Air Conditioner | All sizes | 12 EER | 4. All equipment requires AHRI certification and copy of certificate should be included.

## Lighting Worksheet
page 1 of 2 |  |  |  |  | page 2 of 2
ENERGY REDUCTION WORKSHEET FOR LIGHTING RETROFITS |  |  |  |  | ENERGY REDUCTION WORKSHEET FOR LIGHTING RETROFITS
DO NOT use "see attached" on this spreadsheet. |  |  |  |  | DO NOT use "see attached" on this spreadsheet.
JOB/CUSTOMER NAME: |  |  |  |  | JOB/CUSTOMER NAME: |  | 0
PROJECT LOCATION: |  |  |  |  | PROJECT LOCATION: |  | 0
Description of Improvements |  |  |  |  | Description of Improvements (cont'd)
Type of Improvement: Select an eligible improvement from the drop down boxes below. Open a Type of Improvements only if it is used on the project | Lamp Manf. & Code for CFL's. Lamp Manf. for Full Sized Flourescents, HID's & LED's. Manf. & Brand Name for Exit Signs, Residential Light Fixtures, Traffic Signals, & Ceiling Fans. | Model No. & Type for CFL's. Lamp Code for Full-Size Flourescent, HID's & LED's. Model No. for Exit Signs, Residential Light Fixtures, Traffic Signal, & Ceiling Fans. | Ballast Manufacturer | Ballast Model Number | Fixture Manufacturer. and Fixture Type for Residential Fixtures. and Model Name for Ceiling Fans. | Fixture Model Number, AND list the Quantity in parenthesis | Lamp Watts | Lamps per Fixture | Number of Fixtures (that hold the lamps) | Number of Ballasts | Ballast Factor. For Electronic or No Ballast use 1.00, For Magnetic use 1.15 | Total Lamps | Total Watts | Estimated Cost
| PROPOSED LIGHTING: |  |  |  | PROPOSED LIGHTING (cont'd):
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
Type of Improvement | [10 empty] | 1 | 0 | 0 | 0
EXISTING LIGHTING: |  |  |  |  | EXISTING LIGHTING (cont'd):
Lamp Type: | Brief Description (such as: T12's with magnetic ballasts in old Gym) |  |  |  | Brief Description (cont'd) (such as: T12's with magnetic ballasts in old Gym) |  | Lamp Watts | Lamps per Fixture | Number of Fixtures |  | Ballast Factor (see instructions at top of column) | Total Lamps | Total Watts
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Lamp Type | [10 empty] | 1 | 0 | 0
Estimated Total Cost | A. Sum of Total Watts EXISTING (2) "Total Watts of Old System" | B. Sum of Total Watts PROPOSED (2) | REDUCTION of connected watts "A" minus "B" | PERCENT REDUCTION (1) of connected watts |  | 1. Percent Reduction is equal to; Total Existing Watts, minus the Total Proposed Watts, divided by the Total Existing Watts. |  |  |  | 2. Watts are equal to Lamp Watts, multiplied by the Lamps per Fixture, multiplied by the Number of Fixtures, multyplied by the Ballast Factor.
0 | 0 | 0 | 0 | 0% | D. Total Existing Lamps
|  | C. Total Existing "Number of Fixtures" = | 0 |  | = 0 |  |  | E. Existing "Lamps per Fixture" (D/C)= | #DIV/0! |  |  |  | F. Existing "Lamp Watts" (A/D or A/[CxE])= | #DIV/0!
This spreadsheet may only be used with a computer, and is not for use as a template for a hand written application. The spreadsheet is set up to print on two pages of 8.5 x 11 paper, and must be submitted that way. Do not reformat this spreadsheet. If more room is needed, save under a new name, and use two printouts. If using more than one set of pages, also note that a second, third, fourth, etc., set of pages exist by inputing the the words "1 of X", "2 of X", etc., along with the JOB/CUSTOMER Name and Address.
Type of Improvement | 1 | Lamp Type | total existing lamps:
Compact Flourescent | 1.15 | Incandescent | 0
Induction Flourescent |  | Mercury Vapor
T-5 Flourescent |  | Hologen
T-8 Flourescent |  | Flourescent
High Intensity Discharge (HID) |  | Other
Light Emitting Diode (LED)
LED Exit Sign
Energy Star Residential Fixture
LED Traffic Signal
Energy Star Ceiling Fan